## Slide 1: Measuring Performance & Facilities Management
CIBSE Conference 2025
Session Four - Post Occupancy Evaluation
Tom McNeil

## Slide 2
AGAR GROVE
RAVELIN SPORTS CENTRE
Notes: I’m going to go through 2 very different case study projects which I’ve been fortunate to be involved in and where post occupancy evaluation has been a key part of the process of delivering a successful project.
Both clients wanted very low running costs and high performing buildings
Highlight the benefits of adopting POE on these projects.

## Slide 3
AGAR GROVE
Image Hawkins Brown
Notes: My first mechanical design project.

## Slide 4
AGAR GROVE
COMPLETED 2024
COMPLETED 2024
Image Hawkins Brown
(PHASE 1A)
(PHASE 1B)
(PHASE 1B)
(PHASE 1B)
(PHASE 1C)
(PHASE 1C)

## Slide 5
AGAR GROVE, PHASE 1A
Reference 1. Building Performance Network (BPN) State of the Nation Report, 2020
1
Operational Energy Performance
Notes: Proof of concept
Communal heating – heat losses a problem. Despite being 30%

## Slide 6: Occupant comfort
Q: Generally, how warm would you say your home felt last Summer?
Notes: In addition to energy, the POE ficussed on occupant percenptions and satisfctaion through an occupant survey conducted at the end of the first year of operatiuon. This covered a range of things including summer comfort which is presented here.
2018 London heat waves
Sample of monitoring of internbal temperature and air quality
Duel aspect

## Slide 7: Communal heating
65°C Flow
35°C Return
May 18- Aug 19
Notes: Measured heat loss from the LTHW system (pipes, valves etc.) = 160W/dwelling
~1400kWh losses per dwelling per year
Distribution loss factor = heat generated / heat used by residents = 1.4
30% heat losses.
Camden have a database with all the data

## Slide 8
AGAR GROVE, PHASE 1B
Communal heating temperature reduction (57°C flow)
Summer comfort
Winter comfort
Notes: Communal heating temperature dropped to reduce losses and improve system efficiency and align better for a transition to heat pumps.

## Slide 9
AGAR GROVE, PHASE 1C

## Slide 10: Metering diagram
HEAT ENERGY PRODUCED
BLOCK LEVEL HEAT METER
ASHP ELECTRICAL ENERGY CONSUMED. ASHP 1 + 2
6no. POE DWELLINGS
Notes: Defined success criteria to Collecting lots of Data. This time through a wireless Mbus system

## Slide 11
Notes: Collecting lots of Data. This time through a wirless Mbus system

## Slide 12
Highest heating demand 65 kWh/m2/yr
March 2025
Lowest heating demand 2 kWh/m2/yr
Internal temperature (°C)

## Slide 13
RAVELIN SPORTS CENTRE

## Slide 14: Ravelin Energy Consumption
Notes: Also achieves the net zero carbon buildings standard which for 2028 would dbe around 170 for this type of building.

## Slide 15: Display Energy Certificate

## Slide 16: Design & Delivery
Compact form factor
Extensive daylighting
Mixed-mode ventilation and heat recovery from cooling, ventilation, waste pool water
Leanly sized air source heat pumps
PV array to meet 20% building energy demand
Soft Landings
  DEC A (energy) performance target
  Detailed building performance specification documents
  Remote access to BMS and meter data
  Commissioning and handover support
  2 years of aftercare and POE
Notes: Procurement – 2 stage tender – preferred contractor Wates – priced the job open book. Wates building services inhouse MEP open book. They didn’t go to tier 1 MEP contractor.
Max Fordham MEP did installation drawings. We took on our Stage 4 tender pack and made it all work.
Did a very good job of commissioning. Independent commissioning manager

## Slide 17
Chart: Energy Use Intensity (kWh/m2/yr.)
| Ravelin Measured | CIBSE TM54 estimate
Heating | 38.2657 | 47
Cooling | 2.6944 | 3
Hot Water | 6.1665 | 17
Lift | 0.19078 | 0.2
Small Power | 18.1987 | 21
Lighting | 10.5932 | 11
Auxilliary (Fans, pumps) | 10.8375 | 15
Pool Treatment | 9.4001 | 12
OPERATIONAL ENERGY
Notes: Full access to BMS
We were