## Isolated
CIBSE AM10 Design tool for isolated spaces
Cases 1 and 2 - Single sided ventilation through buoyancy alone
Required flowrate (m3/s) | 0.2
Number of openings
Discharge coefficient | 0.61
Outside temperature (C) | 22
Inside temperature (C) | 26
Vertical distance between openings (m) | 1.2
Size of each opening (m2) | 0.82619
Case 3 - Single sided ventilation through an open window by wind alone
Required flowrate (m3/s) | 0.1
Wind speed at building height (m/s) | 3
Flow coefficient | 0.05
Required area | 0.66667
Case 4 - Cross-flow ventilation by wind alone
Required flowrate (m3/s) | 1
Wind speed at building height (m/s) | 3
Discharge coefficient | 0.61
Wind pressure coefficients
windward side | 0.5
leeward side | -0.2
Required area | 0.92367

## Single-cell
CIBSE AM10 Design tool for single cell buildings (cases 5 and 6)
Temperature data
Outside temperature (C) | 25
Stack temperatures (C)
at a height of X (m) | 10
the temperature is (C) | 31
at ground level it is (C) | 28
Stratification index | 7
Wind data
Met wind speed (m/s) | 0
Building height (m) | 10
Terrain type
Site wind speed (m/s) | 0
Opening data
Opening Number | Height m | Cp | Flow m3/s | Cd | Press drop (Pa) | CdA (m2) | A (m2) | Relative size
1 | 1.85 | 0.25 | 0.448 | 0.61 | 1.0697 | 0.33156 | 0.54354 | 0.6596
2 | 5.1 | 0.25 | 0.448 | 0.61 | 0.69668 | 0.41084 | 0.67351 | 0.81732
3 | 8.35 | 0.25 | 0.448 | 0.61 | 0.29179 | 0.63483 | 1.0407 | 1.2629
Outlet | 11.5 | -0.1 | -1.344 | 0.61 | -0.46539 | 1.508 | 2.4721 | 1
Adjust this slider bar to vary the internal pressure

## Chimney
CIBSE AM10 Design tool for buildings with chimneys
Temperature data
Outside temperature (C) | 25
Room temperature (C) | 28
Chimney data
Chimney temperature (C) | 31
Chimney length (m) | 8
Height of chimney above building (m) | 1.5
Discharge coefficient | 0.8
Wind data
Met wind speed (m/s) | 0
Building height (m) | 10
Terrain type
Site wind speed (m/s) | 0
Opening data
Opening Number | Height m | Cp | Flow m3/s | Cd | Press drop (Pa) | CdA (m2) | A (m2) | Relative size
1 | 1.85 | 0.2 | 0.448 | 0.61 | 1.3947 | 0.29037 | 0.47602 | 0.66103
2 | 5.1 | 0.2 | 0.448 | 0.61 | 1.0223 | 0.33915 | 0.55599 | 0.77209
3 | 8.35 | 0.2 | 0.448 | 0.61 | 0.64997 | 0.42535 | 0.69729 | 0.96831
Chimney outlet |  | -0.15 | -1.344 | 0.8 | -0.60943 | 1.3178 | 1.6473 | 1
Adjust this slider bar to vary the internal pressure

## IAQ
CIBSE AM10 Design tool for IAQ analysis (based on CO2 as proxy)
Room volume (m3) |  | 3000
CO2 emission rate (l/hr.p) |  | 20
Initial CO2 concentration (ppmv) |  | 791.3
Condition set | Outside CO2 ppmv | No. of Occupants | Air change rate (hr-1) | Rate equiv. to 10l/s.p
1 | 350 | 0 | 0.1 | 0
2 | 450 | 100 | 1.2 | 1.2
3 | 450 | 100 | 0.3 | 1.2
4 | 450 | 100 | 4.8 | 1.2
5 | 350 | 0 | 0.25 | 0
Hour beginning | Condition set applying this hour | Concn at end of hour (ppmv) |  |  |  |  | Av. during occupied hours | Occupied hours
0 | 5 | 693.6848 | [5 empty] | 0
1 | 5 | 617.662 | [5 empty] | 0
2 | 5 | 558.4554 | [5 empty] | 0
3 | 5 | 512.3452 | [5 empty] | 0
4 | 5 | 476.4346 | [5 empty] | 0
5 | 5 | 448.4673 | [5 empty] | 0
6 | 5 | 426.6864 | [5 empty] | 0
7 | 5 | 409.7235 | [5 empty] | 0
8 | 3 | 996.1219 |  |  |  |  | 1493.5915 | 1
9 | 3 | 1430.5366 |  |  |  |  | 1493.5915 | 1
10 | 3 | 1752.3589 |  |  |  |  | 1493.5915 | 1
11 | 4 | 598.464 |  |  |  |  | 1493.5915 | 1
12 | 4 | 588.9677 |  |  |  |  | 1493.5915 | 1
13 | 3 | 1128.9093 |  |  |  |  | 1493.5915 | 1
14 | 3 | 1528.9079 |  |  |  |  | 1493.5915 | 1
15 | 3 | 1825.2341 |  |  |  |  | 1493.5915 | 1
16 | 3 | 2044.758 |  |  | Av. concn during occ. hours (ppmv) | 1493.5915 | 1493.5915 | 1
17 | 3 | 2207.3853 |  |  | Max concn during occ. hours (ppmv) | 2327.8626 | 1493.5915 | 1
18 | 3 | 2327.8626 |  |  | Max deviation from average | 55.86% | 1493.5915 | 1
19 | 5 | 1890.3609 | [5 empty] | 0
20 | 5 | 1549.6343 | [5 empty] | 0
21 | 5 | 1284.2761 | [5 empty] | 0
22 | 5 | 1077.615 | [5 empty] | 0
23 | 5 | 916.6671 | [5 empty] | 0
24 | 5 | 791.3208 | [5 empty] | 0
11
Note on B14: AM10: For each hour in the day, allocate one of the condition sets from the above table.
Note on A14: AM10: The number in this column is the time at the beginning of the hour, i.e. the first row of data is the hour from midnight to 01:00 am
Note on A5: AM10: To achieve a repeating cycle, enter the calculated value of the concentration at hour=24 in this cell

## Worksheet
Worksheet |  |  |  | Variable list
|  |  |  | Variable name | Location | Description
Basic data |  |  |  | alpha | =Worksheet!$C$20 | Terrain index exponent
Reference density (kg/m3) | 1.2 |  |  | alpha_c | =Worksheet!$C$59 | Ditto for chimney case
Reference temperature (C) | 18 |  |  | Cd_c | =Chimney!$B$10 | Discharge coefficient for chimney
Gravitational accn (m/s2) | 9.81 |  |  | CO2_emission_rate | =IAQ!$C$4 | Co2 emissions per person
|  |  |  | Condition_set | =IAQ!$A$8:$D$12 | sets of parameters for IAQ analysis
|  |  |  | Cp_1 | ='Single-cell'!$C$19 | Press coefficient on opening 1
Single Cell data |  |  |  | Cp_1c | =Chimney!$C$19 | ditto for chimney case
External density | 1.1718 |  |  | Cp_2 | ='Single-cell'!$C$20 | ditto for 2
Internal density | 1.1601 |  |  | Cp_2c | =Chimney!$C$20 | ditto for chimney case
Ref density difference (kg/m3) | 0.011679 |  |  | Cp_3 | ='Single-cell'!$C$21 | ditto for 3
Terrain data | K | alpha |  | Cp_3c | =Chimney!$C$21 | ditto for chimney case
Open flat country | 0.68 | 0.17 |  | Cp_4 | ='Single-cell'!$C$22 | ditto for 4
Country with scattered windbreaks | 0.52 | 0.2 |  | Cp_4c | =Chimney!$C$22 | ditto for chimney case
Urban | 0.35 | 0.25 |  | Emissions | =Worksheet!$E$81:$E$105 | Profile of CO2 emissions
City | 0.21 | 0.33 |  | g | =Worksheet!$B$6 | gravitational accn
Use meteorological value | 1 | 0 |  | Hcb | =Chimney!$B$13 | Building height in chimney case
Index selected by Terrain combo box | 5 |  |  | hcc | =Chimney!$B$9 | height of chimney
Values used in the analysis | 1 | 0 |  | Initial_CO2_conc | =IAQ!$C$5 | Initial CO2 concn
|  |  |  | Initial_vpm | =Worksheet!$H$81:$H$105 | Array of CO2 concentration at start of each hour
|  |  |  | K | =Worksheet!$B$20 | Terrain index constant
Scroll bars |  |  |  | Kc | =Worksheet!$B$59 | Ditto for chimney case
value of Psi scroll bar (0-1000) | 6147 |  |  | l_c | =Chimney!$B$8 | Length of chimney
Maximum internal pressure (1) | 1.0742 |  |  | Occupants | =Worksheet!$D$81:$D$105 | Profile of no. of occupants
Maximum internal pressure (2) | 0.70115 |  |  | Outside_CO2 | =Worksheet!$C$81:$C$105 | Length of chimney
Maximum internal pressure (3) | 0.29626 |  |  | Pci | =Worksheet!$B$57 | Internal pressure for chimney case
Maximum internal pressure | 0.29606 |  |  | Print_Area | =Worksheet!$E$1:$G$56 | Excel variable
Max internal pressure | -0.46072 |  |  | Psi | =Worksheet!$B$30 | Internal pressure for stack case
Internal pressure | 0.0044701 |  |  | Ref_density_diff | =Worksheet!$B$12 | Density difference inside to outside @ zero height
|  |  |  | rho_c_c | =Worksheet!$B$49 | Density in chimney
Temperature profile | Opng hts (m) | Temp (C) |  | rho_c_e | =Worksheet!$B$47 | Density of outside air chimney case
Heights | 0 | 28 |  | rho_c_r | =Worksheet!$B$48 | Room density chimney case
| 1.85 | 28 |  | rho_e | =Worksheet!$B$10 | density of outside air in single cell case
| 5.1 | 28.0243 |  | rho_ref | =Worksheet!$B$4 | Reference density
| 8.35 | 28.7885 |  | Room_volume | =IAQ!$C$3 | Room vol for IAQ analysis
| 11.5 | 37.7064 |  | Site_wind_speed | ='Single-cell'!$B$14 | Calculated for site
|  |  |  | StratIndex | ='Single-cell'!$B$9 | Generates vertical temp profile
Tout check | 25 |  |  | Tbs | ='Single-cell'!$B$8 | Temp @ bottom of stack
|  |  |  | Tcchimney | =Chimney!$B$7 | Temperature in chimney
Isolated Data |  |  |  | Tcout | =Chimney!$B$4 | Outside temperture for chimney case
Single sided ventilation - no. of openings | 1 |  |  | Tcroom | =Chimney!$B$5 | Room temperature for chimney case
| 2 |  |  | Tnpl | =Worksheet!$C$38 | Temp @ NPL
Selected option | 2 |  |  | Tout | =Worksheet!$B$39 | Temp outside
|  |  |  | Tref | =Worksheet!$B$5 | Temp at which ref density is defined
Chimney Data |  |  |  | Tstack | ='Single-cell'!$B$7 | T in stack at height Z_stack
External density | 1.1718 |  |  | VcMet | =Chimney!$B$12 | Met wind speed chimney case
Room density | 1.1601 | 0.011679 |  | VcSite | =Chimney!$B$15 | Site wind speed chimney case
Chimney density | 1.1487 |  |  | Vmet | ='Single-cell'!$B$11 | Met wind speed
|  |  |  | Volume_flow | =Worksheet!$G$81:$G$105 | Profile of volume flows for IAQ
Internal pressure slider | 4839 |  |  | Z_1 | ='Single-cell'!$B$19 | height of opening 1
Minimum internal pressure | -2.2159 |  |  | Z_1c | =Chimney!$B$19 | ditto for chimney case
Maximum internal pressure (1) | -0.21196 |  |  | Z_2 | ='Single-cell'!$B$20 | ditto for 2
Maximum internal pressure (2) | -0.58432 |  |  | Z_2c | =Chimney!$B$20 | ditto for chimney case
Maximum internal pressure (3) | -0.95668 |  |  | Z_3 | ='Single-cell'!$B$21 | ditto for 3
maximum internal pressure | -0.95688 |  |  | Z_3c | =Chimney!$B$21 | ditto for chimney case
Internal pressure | -1.6067 |  |  | Z_4 | ='Single-cell'!$B$22 | ditto for 4
Terrain class | 5 |  |  | Z_4c | =Chimney!$B$22 | ditto for chimney case
values used in analysis for K and alpha | 1 | 0 |  | Z_b | ='Single-cell'!$B$12 | Building height (for wind speed calcs)
|  |  |  | Z_stack | ='Single-cell'!$B$6 | height at which stack temp is given
IAQ analysis
Hour | Condition set for hour | Outside CO2 vpm | Occupants | Emissions ml/s | air change rate (hr-1) | Volume flow m3/s | Initial vpm | Final vpm
0 | 5 | 350 | 0 | 0 | 0.25 | 0.20833 | 791.3 | 693.6848
1 | 5 | 350 | 0 | 0 | 0.25 | 0.20833 | 693.6848 | 617.662
2 | 5 | 350 | 0 | 0 | 0.25 | 0.20833 | 617.662 | 558.4554
3 | 5 | 350 | 0 | 0 | 0.25 | 0.20833 | 558.4554 | 512.3452
4 | 5 | 350 | 0 | 0 | 0.25 | 0.20833 | 512.3452 | 476.4346
5 | 5 | 350 | 0 | 0 | 0.25 | 0.20833 | 476.4346 | 448.4673
6 | 5 | 350 | 0 | 0 | 0.25 | 0.20833 | 448.4673 | 426.6864
7 | 5 | 350 | 0 | 0 | 0.25 | 0.20833 | 426.6864 | 409.7235
8 | 3 | 450 | 100 | 555.5556 | 0.3 | 0.25 | 409.7235 | 996.1219
9 | 3 | 450 | 100 | 555.5556 | 0.3 | 0.25 | 996.1219 | 1430.5366
10 | 3 | 450 | 100 | 555.5556 | 0.3 | 0.25 | 1430.5366 | 1752.3589
11 | 4 | 450 | 100 | 555.5556 | 4.8 | 4 | 1752.3589 | 598.464
12 | 4 | 450 | 100 | 555.5556 | 4.8 | 4 | 598.464 | 588.9677
13 | 3 | 450 | 100 | 555.5556 | 0.3 | 0.25 | 588.9677 | 1128.9093
14 | 3 | 450 | 100 | 555.5556 | 0.3 | 0.25 | 1128.9093 | 1528.9079
15 | 3 | 450 | 100 | 555.5556 | 0.3 | 0.25 | 1528.9079 | 1825.2341
16 | 3 | 450 | 100 | 555.5556 | 0.3 | 0.25 | 1825.2341 | 2044.758
17 | 3 | 450 | 100 | 555.5556 | 0.3 | 0.25 | 2044.758 | 2207.3853
18 | 3 | 450 | 100 | 555.5556 | 0.3 | 0.25 | 2207.3853 | 2327.8626
19 | 5 | 350 | 0 | 0 | 0.25 | 0.20833 | 2327.8626 | 1890.3609
20 | 5 | 350 | 0 | 0 | 0.25 | 0.20833 | 1890.3609 | 1549.6343
21 | 5 | 350 | 0 | 0 | 0.25 | 0.20833 | 1549.6343 | 1284.2761
22 | 5 | 350 | 0 | 0 | 0.25 | 0.20833 | 1284.2761 | 1077.615
23 | 5 | 350 | 0 | 0 | 0.25 | 0.20833 | 1077.615 | 916.6671
24 | 5 | 350 | 0 | 0 | 0.25 | 0.20833 | 916.6671 | 791.3208
Note on A39: Steve Irving: This check is to avoid a divide by zero if outside and NPL temps are equal (I.e.there is no stack effect)